Water Leak Detection for Non-Raised Floors / CSI Model Specification

TraceTek® TT3000 Large Leak Detection and Location System with Touch Screen Control Panel

Part 1 – General

1.1	Furnish a complete leak detection system including electronic alarm modules, water sensing cable, graphic display map, and auxiliary equipment. The system shall be capable of automatically detecting the presence of water at any point along the continuous length of sensing cable. The system shall sound an alarm and display the location point of liquid contact within .1% of the total connected sensing cable length. No more than one foot of liquid, in contact with a sensing cable at a depth of 1/16 inch, shall be required to cause an audible alarm at the electronic alarm module.

The system shall be UL listed, FM approved, and CSA certified. The system manufacturer shall have at least five years of experience with leak detection and location technology, including both sensing cable and the associated alarm electronics. The manufacturer shall provide written verification of current ISO 9001 registration.

1.2	The system shall be the TraceTek TT1000 Leak Detection and Location System as manufactured by Pentair Thermal management, Menlo Park, California, with factory representation by California Detection Systems, Inc. (714) 692-0015.

Part 2 -Products

2.1	The alarm and locating module (Model TT-TS12) shall be housed in a NEMA 12 enclosure and have a 12” full color, high resolution SVGA display with touch screen, which provides status and alarm data. It shall be capable of monitoring up to 250 external TraceTek leak detection circuits. The alarm and locating module shall continuously monitor all sensing cable for liquid contact. Contact with liquid shall result in an audible alarm, display of the leak location with the name of the reporting channel and the distance along the cable in feet or meters. The leak location information is also used to position a flashing “LEAK” icon over a user designated background image.

The electronic alarm module shall continue to monitor the sensing cable after detection of liquid. It shall re-alarm if the liquid spreads, or if a second leak is detected, more than a specified distance from the original location.

The electronic alarm module shall provide multi-level password protection.

Startup is automatic and should there be a power disruption, the system will pick up where it left off including the re-flashing of any working alarms that have not been cleared or that occurred during the power outage.

The electronic alarm module shall have onboard event history for up to 5,000 events stored in a non-volatile memory. All event history can be downloaded to a USB memory stick in XML format.

The alarm module shall provide a built in Modbus RTU serial interface with user adjustable baud rates and port setup. Modbus/TCP is supported via one of two Ethernet connectors.

2.2	The electronic alarm module shall have the capability of monitoring a total of 250 external TraceTek leak detection circuits. The remote modules may be a combination of sensor interface modules (TTSIM) or relay modules (TT–NRM), or additional wireless Mesh Transmitters.

2.3	The water sensing cable (TT1000) shall be resistant to corrosion. It shall detect the presence of water-based liquids but shall not detect hydrocarbons. The cable shall be constructed of two sensing wires and two insulated wires embedded in a fluoropolymer carrier rod. The sensing wires shall be jacketed with a conductive fluoropolymer. The cable shall be constructed with no metal parts exposed to the environment. Sensing cable shall dry within 15 seconds upon removal from standing water; sensing cable that is braided in construction is not acceptable.

The sensing cable shall have a breaking strength of 160 pounds. It shall have an abrasion resistance of>65 cycles per UL 719. The sensing cables shall be capable of accommodating any number of branches using TraceTek branching connectors (TT -MBC-PC).

2.4	Jumper cable shall be available to interconnect sensing cables or to facilitate remote mounting of the electronic alarm module. Jumper cable may not add more than 0.01% of additional length to the leak detection circuit.

2.5	All sensing and jumper cable shall meet the requirements of NFPA 262 “Standard Method of Test for Flame Travel and Smoke of Wires and Cables for use in Air-Handling Spaces”.

2.6	The manufacturer shall provide modular lengths of sensing cable, jumper cable, and system components with electrical connectors that have been pre-installed and tested at the factory.  Field splicing is not acceptable.

Part 3 -Execution

3.1	All TraceTek System components shall be installed in accordance with the manufacturer's installation instructions, NEC, and local code requirements.

3.2	The sensing cable shall be installed after all piping, air conditioning, and other mechanical work has been completed. The floor sensing cable path shall remain clear of water, oil, solder, flux, dirt or other materials that may soil the sensing cable.

3.3	The sensing cable shall be secured to the floor with plastic hold-down clips (TT-HDC-1/4) on approximately six-foot intervals.

3.4	The sensing cable installer shall be responsible for installation of the sensing cable, functional testing, and mapping of the system. Tyco Thermal Controls or its trained local representative shall provide supervision and training.

3.5	Upon completion of the system installation, a factory pre-connectorized, five foot long, water-sensing cable shall be temporarily installed at the far end of each leak detection circuit. The sensing cable shall be immersed in approximately one foot of water, at a depth of 1/8 inch, to confirm that an audible alarm is generated at the alarm module and that the appropriate distance to the leak is displayed. The installer shall perform and certify the tests in the presence of the owner's representative.

3.6	A graphic display map, prepared from “as- built” drawings, shall be furnished upon completion. The map shall indicate the location of the sensing cables, landmarks such as equipment, A/C units, walls, floor drains, change of cable direction, and cable distance readings. The map shall be mounted next to the alarm and locating module.