Leak Detection for Fuel in Double Contained Tanks / CSI Model Specification

TraceTek® TT5000 Small Non-locating Leak Detection System

Part 1 – General

1.1	Furnish a complete leak detection system including electronic alarm modules, sensing cables, and auxiliary equipment. The system shall be capable of automatically detecting the presence of liquid at any point along the continuous length of sensing cable. The system shall sound an alarm, and indicate the leak with an LED. No more than one foot of liquid, in contact with a sensing cable at a depth of 1/16 inch, shall be required to cause an audible alarm at the electronic alarm module.

1.2	The system shall be UL Listed, FM approved, and tested to Third Party Procedures developed according to the U.S. EPA’s “Standard Test Procedures for Evaluating Leak Detection Methods: Interstitial Detector (Liquid Phase) and Liquid-Phase Out-of-Tank Product Detector”.

The system manufacturer shall have at least five years of experience with leak detection and location technology, including both sensing cable and the associated alarm electronics. The manufacturer shall provide written verification of current ISO 9001 registration.

1.3	The system shall be the TraceTek TT5000 Leak Detection and Location System manufactured by Tyco Thermal Controls, Menlo Park, California, distributed by California Detection Systems, Inc. (714) 692-0015.

Part 2 -Products

2.1	The alarm module (Model TTA-SIM-1A) shall be housed in a NEMA 1. It shall be capable of monitoring up to 500 feet of TraceTek sensing cable. The alarm module shall continuously monitor all sensing cable for liquid contact. Contact with liquid shall result in an audible alarm, illumination of a "leak" LED, and actuation of an output relay.

The electronic alarm module shall continue to monitor the sensing cable after detection of liquid. It shall re-alarm if the liquid spreads, or if a second leak is detected, more than a specified distance from the original location.

The complete system shall be continuously monitored for electrical continuity. The loss of continuity in any of the wires shall result in an audible alarm, illumination of a "fault" LED, and actuation of an output relay.

The electronic alarm modules shall require no operator programming and shall automatically calibrate whenever power is applied.

The alarm module shall be capable of digitally communicating to host systems via RS 485, at the user's option.

The alarm module shall be tested and found to comply with the limits for a Class B digital device, pursuant to FCC, Part 15.

The alarm module shall operate on 120V AC, 60 Hz. single-phase power. Each module will require a dedicated 15 amp, 120 VAC circuit.

2.2	The fuel oil sensing cable (TT5000) shall ignore the presence of water. The preconnectorized fuel oil sensors shall only respond to liquid and vapor phase hydrocarbon in concentrations above 25,000 PPM. No more than 4” of wetted length is required for an alarm regardless of sensor length.

2.3	Jumper cable shall be available to interconnect sensing cables or to facilitate remote mounting of the electronic alarm module. Jumper cable may not add more than 0.01% of additional length to the leak detection circuit.

2.4	All sensing and jumper cable shall pass UL 910, Test Method for Fire and Smoke Characteristics of Electrical and Optical-Fiber Cables Used in Air-Handling Spaces, and shall be Class 2 plenum cable per NEC 725-51 (a).

Part 3 -Execution

3.1	All TraceTek system components shall be installed in accordance with the manufacturer's installation instructions. The tank installer shall be responsible for providing a clean and dry containment system with adequate clearance to install the sensing cable system. The sensing cable installer shall be responsible for installation of the sensing cable system, functional testing, and mapping of the system. The system manufacturer or its trained local representative shall provide supervision and training.

3.2	Upon completion of the system installation, a factory pre-connectorized, five-foot-long sensing cable shall be temporarily installed at the far end of the leak detection circuit. The fuel sensor shall be immersed in approximately one foot of the appropriate fuel at a depth of one-eighth inch to confirm that an alarm is generated and the appropriate distance is indicated on the electronic module. The installer shall perform and certify the tests in the presence of the owner's representative.