Leak Detection For Chemical Storage / CSI Model Specification

TraceTek® Small Leak Detection and Location System

Part 1 – General

1.1	Furnish a complete leak detection system including electronic alarm modules, water sensing cable, graphic display map, and auxiliary equipment. The system shall be capable of automatically detecting the presence of liquid at any point along the continuous length of sensing cable. The system shall sound an alarm and locate, with an LCD display, the point of liquid contact within .5% of the total connected sensing cable length. No more than one foot of liquid, in contact with a sensing cable at a depth of 1/16 inch, shall be required to cause an audible alarm at the electronic alarm module.

1.2	The system shall be UL Listed, FM approved, and tested to Third Party Procedures developed according to the U.S. EPA’s “Standard Test Procedures for Evaluating Leak Detection Methods: Interstitial Detector (Liquid Phase) and Liquid-Phase Out-of-Tank Product Detector”.

The system manufacturer shall have at least five years of experience with leak detection and location technology, including both sensing cable and the associated alarm electronics. The manufacturer shall provide written verification of current ISO 9001 registration.

1.3	The system shall be manufactured by Tyco Thermal Controls, TraceTek Products Group, Menlo Park, California, distributed by California Detection Systems, Inc. (714) 692-0015.

Part 2 -Products

2.1	The alarm and locating module (Model TTA-SIM-2) shall be housed in a NEMA 1 enclosure and have a 4 line x 20 character, backlit LCD display, which provides status and alarm data. It shall be capable of monitoring up to 500 feet of TraceTek sensing cable. The alarm and locating module shall continuously monitor all sensing cable for liquid contact. Contact with liquid shall result in an audible alarm, illumination of a "leak" LED, actuation of an output relay, and a digital display of the distance to the liquid location.

The electronic alarm module shall continue to monitor the sensing cable after detection of liquid. It shall re-alarm if the liquid spreads, or if a second leak is detected, more than a specified distance from the original location.

The complete system shall be continuously monitored for electrical continuity. The loss of continuity in any of the wires shall result in an audible alarm, illumination of a "fault" LED, and actuation of an output relay.

The electronic alarm modules shall require no operator programming and shall automatically calibrate whenever power is applied.

The alarm module shall be capable of digitally communicating to host systems via RS 485, at the user's option.

The alarm module shall be tested and found to comply with the limits for a Class B digital device, pursuant to FCC, Part 15.

The alarm module shall operate on 120 VAC, 60 Hz, single-phase power. Modules shall be provided with dedicated 120 VAC circuits.

2.2	The sensing cables shall detect the presence of the type of liquid for which the cable was designed (TT3000, TT5000 and/or TT5001). The cable shall be constructed with no metal parts exposed to the environment.

The sensing cables shall be capable of accommodating any number of branches using TraceTek branching connectors (TT -MBC-MC).

2.3	Jumper cable shall be available to interconnect sensing cables or to facilitate remote mounting of the electronic alarm module.

2.4	A TraceTek portable test box (TT-PTB-1000) shall be provided to the leak detection system installer. It shall become the property of the owner, upon system acceptance, for use in the ongoing preventive maintenance of the leak detection system.

Part 3 -Execution

3.1	All TraceTek system components shall be installed in accordance with the manufacturer's installation instructions. The sensing cable installer shall be responsible for installation of the sensing cable, functional testing, and mapping of the system.  Tyco Thermal Controls or its trained local representative shall provide supervision and training.

3.2	The sensors shall be attached to either vertical or horizontal surfaces as required.

3.3	Upon completion of the system installation, a factory pre-connectorized, five-foot-long sensing cable shall be temporarily installed at the far end of the leak detection circuit. The sensor shall be immersed in approximately one foot of the appropriate liquid at a depth of one-eighth inch to confirm that an alarm is generated and the appropriate distance is indicated on the electronic module. The installer shall perform and certify the tests in the presence of the owner's representative.

3.4	A graphic display map prepared from "as built" drawings shall be furnished upon completion. The map shall indicate the location of each sensing cable, landmarks such as equipment, change of cable direction, and it’s zone number, per the manufacturer’s instructions. The map shall be mounted next to the alarm and locating module.